## Direct Acting PRV
CLA-VAL UK Tel: 01892 514400 Email: info@cla-val.co.uk
Pressure Reducing Valve - SIZING GUIDE - Version 1.0
ENTER THE FOLLOWING SIZING PARAMETERS:
PROJECT REF: | Enter project ref here..
Flow unit: [1] = l/s [2] = m3/h [3] = l/min |  | 1
MINIMUM Flow (Q min.) : | l/s | 0
MAXIMUM Flow (Q max.) : | l/s | 1.5
MINIMUM Inlet pressure: | Bar | 6
MAXIMUM Inlet pressure: | Bar | 6
Outlet Pressure: | Bar | 3
Other Cv : | [l/s] | 0
Enter notes here..
SIZING RULES:
Velocity 2m/s MAX, Pressure drop ratio 3 to 1 MAX |  |  | Click image to view datasheet
Size [inches] | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2"
Size [mm] | 15 | 20 | 25 | 32 | 40 | 50
Kvs [M3/h] | 3 | 3.5 | 6.7 | 7.6 | 12.5 | 15
Velocity [m/s] | 8.4877 | 4.7743 | 3.0556 | 1.865 | 1.1936 | 0.76389
Valve Selection | Velocity High | Velocity High | Velocity High | OK | OK | OK
Valve Model | AQUA-PRV/SC-SP | [5 empty] | cj246
PRV Downstream pressure range: | 1 - 8 bar
Calculations
Flow l/s |  | 1.5
Pressure

## Pilot Operated PRV
CLA-VAL UK Tel: 01892 514400 Email: info@cla-val.co.uk
Pressure Reducing Valve - SIZING GUIDE - Version 1.0
ENTER THE FOLLOWING SIZING PARAMETERS
PROJECT REF: | Enter project ref here..
Flow unit: [1] = l/s [2] = m3/h [3] = L/min |  | 1
Pressure unit: [1] = bar [2] = mhd |  | 1
MINIMUM Flow (Q min.) : | l/s | 0 | Model: NGE-B90-01/LFS |  |  |  |  | Size: | 50 | mm
MAXIMUM Flow (Q max.) : | l/s | 3
MINIMUM Inlet pressure: | bar | 6
MAXIMUM Inlet pressure: | bar | 6
Outlet Pressure: | bar | 3
Other Cv : | [l/s] | 0
Enter notes here…
SUGGESTED SERIES AND SIZES EITHER: | NGE-B90-01/LFS | 50
OR: | B90GE-01/LFS | 32
ENTER YOUR SIZE / SERIES PREFERENCES BELOW
Body pattern [1] Globe [2] Angle | [1 / 2] | 1
Valve series: [1] B-90GE-01/LFS or [2] NGE-B90-01/LFS | [1 / 2] | 2
Selected Valve size (mm): |  | 50
SUMMARY OF SELECTED VALVE
Valve size [mm]: | 50
Model*: | NGE-B90-01/LFS | [13 empty] | cj246
Kvs [m3/h]: | 32 |  | Click image to view datasheet
Downstream Adjustment Range**: | 1.4 - 7.2 bar
Technical Data | Min Flow | Max Flow
Valve % Cv | 0 | 19.245
Valve % Open | 0 | 34.0599
Velocity [m/s] | 0 | 1.5278
Headloss wide open valve [bar] | 0 | 0.11117
Stem lift [mm] | 0 | 3.406
NOTE
*Model B90GE-01/LFS is a Fully ported valve - Example: 100mm Valve has 100mm Flanges and 100mm internals
*Model B-NGE90-01/LFS is a Reduced ported valve - Example: 100mm Valve has 100mm Flanges and 80mm Internals
**Adjustment Ranges available include: 0.1 - 2 bar / 1.4 - 7.2 bar / 2 - 20 bar
Valve CV (l/s) | 48 | 9 | 32
Computed K | [-] | 9.526
Maximum Valve stem lift | [mm] | 10
Valve Seat size | [mm] | 40
ADDITIONAL INFORMATION
Opening Curve | Extrapolation | [12 empty] | l | l | Re
Total volume | [l] | 0.075 | [11 empty] | C.-W. | Nikur. | [/1000]
Removed volume | [l] | 0.025545 | [11 empty] | #DIV/0! | #DIV/0! | 0
| K | DH | Section | V seat | [9 empty] | 0.032148 | 0.019104 | 66.4255
| [-] | [m] | [cm2] | [m/s]
Q max. | 257.2016 | 30.0171 | 42.801 | 0
Q min. |  | #VALUE! | 0
cavitation warning - GE / NGE | 5
Pressure Inlet max | 6
Pressure Inlet Min | 6
Pressure Outlet | 3
Differential pressure | 3
Valve type | 50
Flow unit l/s min | 0 | [16 empty] | #N/A | [6 empty] | #VALUE!
Flow unit l/s max | 3 | Cv^1 | Cv^2 | Cv^3 | Cv^4 | Cv^5 | Remarques |  | K | Vol | Course | Siège
Vanne recherchée | 9 | 3.289 | -11.948 | 25.519 | -24.878 | 9.021 | Extrapolation |  |  | 0.075 | 10 | 40 | Dessin
[13 empty] | Cv | Ouv. | Tra. |  | DN | Max CV | Max OPEN | Min CV | Min OPEN | Velocity | Computed K | Wide open | NGE | #N/A | 2
Code vanne | Cv [l/s] | Cv^1 | Cv^2 | Cv^3 | Cv^4 | Cv^5 | Remarques |  | K | Vol | Course | Siège | 0 | 0 | 0 | 70 |  | % | % | % | % | (m/s) |  | head-loss (mhd) | GE | #N/A | #N/A
11032 | 7.2 | 3.066 | -10.597 | 22.399 | -22.629 | 8.763 | Extrapolation |  | 2.4972 | 0.075 | 10 | 32 | 1 | 3.172 | 3.172 | 70 | 32 | 24.0563 | 36.7415 | 0 | 0 | 3.7299 | 2.4972 | 1.7707 | 36.7415 | * | 1
11040 | 7.7 | 3.066 | -10.597 | 22.399 | -22.629 | 8.763 | Extrapolation |  | 5.3306 | 0.075 | 10 | 40 | 2 | 6.1201 | 6.1201 | 70 | 40 | 22.4942 | 35.5527 | 0 | 0 | 2.3872 | 5.3306 | 1.5482 | 35.5527 | * | 1
11050 | 13 | 3.066 | -10.597 | 22.399 | -22.629 | 8.763 | Test |  | 4.5657 | 0.12 | 15 | 50 | 3 | 8.8586 | 8.8586 | 70 | 50 | 13.3235 | 26.6598 | 0 | 0 | 1.5278 | 4.5657 | 0.54317 | 26.6598 | * | 1
11065 | 20 | 2.833 | -8.601 | 15.932 | -13.823 | 4.662 | Test |  | 5.5095 | 0.16 | 18 | 65 | 4 | 11.4014 | 11.4014 | 70 | 65 | 8.6603 | 19.0431 | 0 | 0 | 0.90402 | 5.5095 | 0.22949 | 19.0431 | * | 1
11080 | 28 | 3.521 | -14.369 | 32.14 | -32.811 | 12.52 | Test |  | 6.45 | 0.3 | 20 | 80 | 5 | 13.7617 | 13.7617 | 70 | 80 | 6.1859 | 16.9961 | 0 | 0 | 0.59679 | 6.45 | 0.11709 | 16.9961 | * | 1
11100 | 48 | 3.568 | -17.025 | 42.239 | -46.985 | 19.203 | Test |  | 5.3584 | 0.64 | 28 | 100 | 6 | 15.9524 | 15.9524 | 70 | 100 | 3.6084 | 10.8487 | 0 | 0 | 0.38195 | 5.3584 | 0.039842 | 10.8487 | * | 1
11150 | 111 | 3.828 | -17.004 | 39.752 | -42.219 | 16.644 | Test |  | 5.0726 | 2 | 43 | 150 | 7 | 17.9856 | 17.9856 | 70 | 150 | 1.5604 | 5.5741 | 0 | 0 | 0.16975 | 5.0726 | 0.0074503 | 5.5741 | * | 1
11200 | 185 | 3.039 | -11.855 | 27.025 | -29.184 | 11.974 | Test |  | 5.7715 | 4.8 | 57 | 200 | 8 | 19.8729 | 19.8729 | 70 | 200 | 0.93624 | 2.7435 | 0 | 0 | 0.095487 | 5.7715 | 0.0026821 | 2.7435 | * | 1
11250 | 299 | 2.626 | -8.666 | 18.271 | -19.053 | 7.822 | Test |  | 5.3943 | 9.5 | 71 | 250 | 9 | 21.6256 | 21.6256 | 70 | 250 | 0.57928 | 1.4925 | 0 | 0 | 0.061111 | 5.3943 | 0.0010268 | 1.4925 | * | 1
11300 | 414 | 1.894 | -4.905 | 11.446 | -14.357 | 6.921 | Test |  | 5.8344 | 15.1 | 86 | 300 | 10 | 23.2541 | 23.2541 | 70 | 300 | 0.41837 | 0.78389 | 0 | 0 | 0.042439 | 5.8344 | 0.00053558 | 0.78389 | * | 1
11350 | 553 | 2.383 | -9.084 | 23.606 | -29.303 | 13.393 | Test |  | 6.0581 | 24.6 | 100 | 350 | 11 | 24.7688 | 24.7688 | 70 | 350 | 0.31321 | 0.73754 | 0 | 0 | 0.031179 | 6.0581 | 0.00030017 | 0.73754 | * | 1
11400 | 706 | 1.41 | -4.619 | 16.072 | -23.937 | 12.066 | Test |  | 6.3408 | 36.2 | 114 | 400 | 12 | 26.1791 | 26.1791 | 70 | 400 | 0.24533 | 0.34316 | 0 | 0 | 0.023872 | 6.3408 | 0.00018417 | 0.34316 | * | 1
12040 | 7 | 3.066 | -10.597 | 22.399 | -22.629 | 8.763 | Extrapolation |  | 6.45 | 0.075 | 10 | 40 | 13 | 27.4944 | 27.4944 | 70 | 40 | 24.7436 | 37.2472 | 0 | 0 | 2.3872 | 6.45 | 1.8734 | 37.2472 | * | 2
12050 | 16 | 3.066 | -10.597 | 22.399 | -22.629 | 8.763 | Test |  | 3.0141 | 0.12 | 15 | 50 | 14 | 28.7231 | 28.7231 | 70 | 50 | 10.8253 | 23.3158 | 0 | 0 | 1.5278 | 3.0141 | 0.35858 | 23.3158 | * | 2
12065 | 24 | 2.833 | -8.601 | 15.932 | -13.823 | 4.662 | Test |  | 3.826 | 0.16 | 18 | 65 | 15 | 29.8737 | 29.8737 | 70 | 65 | 7.2169 | 16.528 | 0 | 0 | 0.90402 | 3.826 | 0.15937 | 16.528 | * | 2
12080 | 33 | 3.521 | -14.369 | 32.14 | -32.811 | 12.52 | Test |  | 4.6435 | 0.3 | 20 | 80 | 16 | 30.9539 | 30.9539 | 70 | 80 | 5.2486 | 14.9624 | 0 | 0 | 0.59679 | 4.6435 | 0.084293 | 14.9624 | * | 2
12100 | 57 | 3.568 | -17.025 | 42.239 | -46.985 | 19.203 | Test |  | 3.7998 | 0.64 | 28 | 100 | 17 | 31.971 | 31.971 | 70 | 100 | 3.0387 | 9.3846 | 0 | 0 | 0.38195 | 3.7998 | 0.028253 | 9.3846 | * | 2
12150 | 130 | 3.828 | -17.004 | 39.752 | -42.219 | 16.644 | Test |  | 3.6982 | 2 | 43 | 150 | 18 | 32.932 | 32.932 | 70 | 150 | 1.3323 | 4.8076 | 0 | 0 | 0.16975 | 3.6982 | 0.0054317 | 4.8076 | * | 2
12200 | 238 | 3.039 | -11.855 | 27.025 | -29.184 | 11.974 | Test |  | 3.4872 | 4.8 | 57 | 200 | 19 | 33.8434 | 33.8434 | 70 | 200 | 0.72775 | 2.1499 | 0 | 0 | 0.095487 | 3.4872 | 0.0016206 | 2.1499 | * | 2
12250 | 378 | 2.626 | -8.666 | 18.271 | -19.053 | 7.822 | Test |  | 3.3751 | 9.5 | 71 | 250 | 20 | 34.7114 |  | 70 | 250 | 0.45821 | 1.1853 | 0 | 0 | 0.061111 | 3.3751 | 0.00064245 | 1.1853 | * | 2
12300 | 601 | 1.894 | -4.905 | 11.446 | -14.357 | 6.921 | Test |  | 2.7685 | 15.1 | 86 | 300 | 21 | 35.5416 |  | 70 | 300 | 0.28819 | 0.54179 | 0 | 0 | 0.042439 | 2.7685 | 0.00025414 | 0.54179 | * | 2
12350 | 735 | 2.383 | -9.084 | 23.606 | -29.303 | 13.393 | Test |  | 3.4294 | 24.6 | 100 | 350 | 22 | 36.3394 |  | 70 | 350 | 0.23565 | 0.55655 | 0 | 0 | 0.031179 | 3.4294 | 0.00016992 | 0.55655 | * | 2
12400 | 1009 | 1.41 | -4.619 | 16.072 | -23.937 | 12.066 | Test |  | 3.1044 | 36.2 | 114 | 400 | 23 | 37.1098 |  | 70 | 400 | 0.17166 | 0.24069 | 0 | 0 | 0.023872 | 3.1044 | 9.0165e-05 | 0.24069 | * | 2
21050 | 9 | 3.289 | -11.948 | 25.519 | -24.878 | 9.021 | Extrapolation |  | 9.526 | 0.075 | 10 | 40 | 24 | 37.8574 |  | 70 | 50 | 19.245 | 34.0599 | 0 | 0 | 1.5278 | 9.526 | 1.1333 | 34.0599 | * | 2
21065 | 12 | 3.289 | -11.948 | 25.519 | -24.878 | 9.021 | Extrapolation |  | 15.304 | 0.12 | 15 | 50 | 25 | 38.5864 |  | 70 | 65 | 14.4338 | 29.2313 | 0 | 0 | 0.90402 | 15.304 | 0.63747 | 29.2313 | * | 2
21080 | 16 | 3.289 | -11.948 | 25.519 | -24.878 | 9.021 | Test |  | 19.7531 | 0.12 | 15 | 50 | 26 | 39.3009 |  | 70 | 80 | 10.8253 | 24.512 | 0 | 0 | 0.59679 | 19.7531 | 0.35858 | 24.512 | * | 2
21100 | 33 | 3.296 | -12.084 | 25.783 | -25.023 | 9.031 | Test |  | 11.3367 | 0.3 | 20 | 80 | 27 | 40.0044 |  | 70 | 100 | 5.2486 | 14.3248 | 0 | 0 | 0.38195 | 11.3367 | 0.084293 | 14.3248 | * | 2
21125 | 45 | 3.296 | -12.084 | 25.783 | -25.023 | 9.031 | Extrapolation |  | 14.8844 | 0.64 | 28 | 100 | 28 | 40.7001 |  | 70 | 125 | 3.849 | 11.0377 | 0 | 0 | 0.24445 | 14.8844 | 0.045331 | 11.0377 | * | 2
21150 | 58 | 2.877 | -9.973 | 20.721 | -19.883 | 7.262 | Test |  | 18.5791 | 0.64 | 28 | 100 | 29 | 41.3912 |  | 70 | 150 | 2.9863 | 7.7558 | 0 | 0 | 0.16975 | 18.5791 | 0.027288 | 7.7558 | * | 2
21200 | 133 | 3.234 | -12.832 | 28.414 | -28.829 | 11.015 | Test |  | 11.1669 | 2 | 43 | 150 | 30 | 42.0802 |  | 70 | 200 | 1.3023 | 4.0002 | 0 | 0 | 0.095487 | 11.1669 | 0.0051894 | 4.0002 | * | 2
21250 | 222 | 3.174 | -11.831 | 24.445 | -23.213 | 8.431 | Test |  | 9.7852 | 4.8 | 57 | 200 | 31 | 42.7697 |  | 70 | 250 | 0.7802 | 2.4055 | 0 | 0 | 0.061111 | 9.7852 | 0.0018626 | 2.4055 | * | 2
21300 | 359 | 2.944 | -11.105 | 23.03 | -21.896 | 8.032 | Test |  | 7.7591 | 9.5 | 71 | 250 | 32 | 43.4616 |  | 70 | 300 | 0.48247 | 1.3948 | 0 | 0 | 0.042439 | 7.7591 | 0.00071225 | 1.3948 | * | 2
21350 | 455 | 2.944 | -11.105 | 23.03 | -21.896 | 8.032 | Test |  | 8.9488 | 15.1 | 86 | 300 | 33 | 44.158 |  | 70 | 350 | 0.38067 | 1.1047 | 0 | 0 | 0.031179 | 8.9488 | 0.0004434 | 1.1047 | * | 2
21400 | 497 | 3.26 | -12.715 | 25.388 | -22.457 | 7.53 | Test |  | 12.7951 | 15.1 | 86 | 300 | 34 | 44.8604 |  | 70 | 400 | 0.3485 | 1.1208 | 0 | 0 | 0.023872 | 12.7951 | 0.00037163 | 1.1208 | * | 2
21500 | 847 | 3.26 | -12.715 | 25.388 | -22.457 | 7.53 | Extrapolation |  | 10.7554 | 36.2 | 114 | 400 | 35 | 45.5702 |  | 70 | 500 | 0.20449 | 0.66135 | 0 | 0 | 0.015278 | 10.7554 | 0.00012795 | 0.66135 | * | 2
21600 | 895 | 3.26 | -12.715 | 25.388 | -22.457 | 7.53 | Extrapolation |  | 19.9744 | 36.2 | 114 | 400 | 36 | 46.2885 |  | 70 | 600 | 0.19353 | 0.62615 | 0 | 0 | 0.01061 | 19.9744 | 0.0001146 | 0.62615 | * | 2
21700 | 1748 | 2.49 | -9.926 | 23.417 | -24.916 | 9.938 | Test |  | 9.7012 | 125 | 155 | 600 | 37 | 47.0164 |  | 70 | 700 | 0.099088 | 0.24576 | 0 | 0 | 0.0077948 | 9.7012 | 3.0043e-05 | 0.24576 | * | 2
31080 | 15.2 | 3.289 | -11.948 | 25.519 | -24.878 | 9.021 | Test |  | 21.8871 | 0.12 | 15 | 50 | 38 | 47.7545 |  | 70 | 80
31100 | 33 | 3.296 | -12.084 | 25.783 | -25.023 | 9.031 | Test |  | 11.3367 | 0.3 | 20 | 80 | 39 | 48.5034 |  | 70 | 100
31150 | 53 | 2.877 | -9.973 | 20.721 | -19.883 | 7.262 | Test |  | 22.2499 | 0.64 | 28 | 100 | 40 | 49.2634 |  | 70 | 150
31200 | 118 | 3.234 | -12.832 | 28.414 | -28.829 | 11.015 | Test |  | 14.1864 | 2 | 43 | 150 | 41 | 50.0347 |  | 70 | 200
31250 | 230 | 3.174 | -11.831 | 24.445 | -23.213 | 8.431 | Test |  | 9.1163 | 4.8 | 57 | 200 | 42 | 50.8173 |  | 70 | 250
31300 | 358 | 2.944 | -11.105 | 23.03 | -21.896 | 8.032 | Test |  | 7.8025 | 9.5 | 71 | 250 | 43 | 51.6111 |  | 70 | 300
31400 | 520 | 3.26 | -12.715 | 25.388 | -22.457 | 7.53 | Test |  | 11.6882 | 15.1 | 86 | 300 | 44 | 52.4157 |  | 70 | 400
31500 | 840 | 3.26 | -12.715 | 25.388 | -22.457 | 7.53 | Extrapolation |  | 10.9354 | 36.2 | 114 | 400 | 45 | 53.2308 |  | 70 | 500
31600 | 860 | 3.26 | -12.715 | 25.388 | -22.457 | 7.53 | Extrapolation |  | 21.6333 | 36.2 | 114 | 400 | 46 | 54.0558 |  | 70 | 600
32100 | 33 | 3.296 | -12.084 | 25.783 | -25.023 | 9.031 | Extrapolation |  | 11.3367 | 0.3 | 20 | 80 | 47 | 54.8901 |  | 70 | 100
32150 | 56 | 2.877 | -9.973 | 20.721 | -19.883 | 7.262 | Extrapolation |  | 19.9298 | 0.64 | 28 | 100 | 48 | 55.7329 |  | 70 | 150
32200 | 133 | 3.234 | -12.832 | 28.414 | -28.829 | 11.015 | Extrapolation |  | 11.1669 | 2 | 43 | 150 | 49 | 56.5834 |  | 70 | 200
[13 empty] | 50 | 57.4406 |  | 70
[13 empty] | 51 | 58.3037 |  | 70
[13 empty] | 52 | 59.1715 |  | 70
32 | [12 empty] | 53 | 60.0429 |  | 70 | bar: 0 3
40 | 0 3: 2 | [6 empty] | 54 | 60.917 |  | 70
50 | [12 empty] | 55 | 61.7924 |  | 70
65 | [12 empty] | 56 | 62.6681 |  | 70
80 | [12 empty] | 57 | 63.5429 |  | 70
100 | [12 empty] | 58 | 64.4157 |  | 70
150 | [12 empty] | 59 | 65.2854 |  | 70
200 | [12 empty] | 60 | 66.1508 |  | 70
250 | [12 empty] | 61 | 67.0109 |  | 70
300 | [12 empty] | 62 | 67.8648 |  | 70
350 | [12 empty] | 63 | 68.7114 |  | 70
400 | [12 empty] | 64 | 69.5499 |  | 70
500 | [12 empty] | 65 | 70.3795 |  | 70
600 | [12 empty] | 66 | 71.1996 |  | 70
700 | [12 empty] | 67 | 72.0096 |  | 70
[13 empty] | 68 | 72.809 |  | 70
[13 empty] | 69 | 73.5975 |  | 70
[13 empty] | 70 | 74.3749 |  | 70
[13 empty] | 71 | 75.1411 |  | 70
[13 empty] | 72 | 75.8964 |  | 70
[13 empty] | 73 | 76.6409 |  | 70
[13 empty] | 74 | 77.3752 |  | 70
[13 empty] | 75 | 78.0999 |  | 70
[13 empty] | 76 | 78.8159 |  | 70
[13 empty] | 77 | 79.5243 |  | 70
[13 empty] | 78 | 80.2264 |  | 70
[13 empty] | 79 | 80.9237 |  | 70
[13 empty] | 80 | 81.618 |  | 70
[13 empty] | 81 | 82.3115 |  | 70
[13 empty] | 82 | 83.0064 |  | 70
[13 empty] | 83 | 83.7053 |  | 70
[13 empty] | 84 | 84.4111 |  | 70
[13 empty] | 85 | 85.127 |  | 70
[13 empty] | 86 | 85.8565 |  | 70
[13 empty] | 87 | 86.6035 |  | 70
[13 empty] | 88 | 87.3721 |  | 70
[13 empty] | 89 | 88.1668 |  | 70
[13 empty] | 90 | 88.9925 |  | 70
[13 empty] | 91 | 89.8545 |  | 70
[13 empty] | 92 | 90.7582 |  | 70
[13 empty] | 93 | 91.7098 |  | 70
[13 empty] | 94 | 92.7156 |  | 70
[13 empty] | 95 | 93.7824 |  | 70
[13 empty] | 96 | 94.9175 |  | 70
[13 empty] | 97 | 96.1284 |  | 70
[13 empty] | 98 | 97.4234 |  | 70
[13 empty] | 99 | 98.8109 |  | 70
[13 empty] | 100 | 100 |  | 70
[16 empty] | NGE SERIES |  |  | GE SERIES
[16 empty] | 50 |  |  | 32
[16 empty] | 0.24576 | 700 |  | 0.34316 | 400
[16 empty] | 0.62615 | 600 |  | 0.73754 | 350
[16 empty] | 0.66135 | 500 |  | 0.78389 | 300
[16 empty] | 1.1208 | 400 |  | 1.4925 | 250
[16 empty] | 1.1047 | 350 |  | 2.7435 | 200
[16 empty] | 1.3948 | 300 |  | 5.5741 | 150
[16 empty] | 2.4055 | 250 |  | 10.8487 | 100
[16 empty] | 4.0002 | 200 |  | 16.9961 | 80
[16 empty] | 7.7558 | 150 |  | 19.0431 | 65
[16 empty] | 14.3248 | 100 |  | 26.6598 | 50
[16 empty] | 24.512 | 80 |  | 35.5527 | 40
[16 empty] | 29.2313 | 65 |  | 36.7415 | 32
[16 empty] | 34.0599 | 50
34.0599
PRV SIZING
[28 empty] | Date : | 2022-01-06
[28 empty] | Proj Ref. : | ENTER PROJECT REF HERE..
BASIC DATA
[29 empty] | Valve size : |  | [mm] | 50
[29 empty] | Valve Series: |  |  | NGE-B90-01/LFS
[29 empty] | Body Pattern: |  |  | GLOBE
[29 empty] | Norm. / Rev. flow : |  |  | NORMAL
[29 empty] | Adjustment Range: |  |  | 1.4 - 7.2 bar
[29 empty] | Q min. : |  | l/s | 0
[29 empty] | Q max. : |  | l/s | 3
[29 empty] | P Inlet @ Min. flow : |  | bar | 6
[29 empty] | P Inlet @ Max. flow : |  | bar | 6
[29 empty] | P Outlet : |  | bar | 3
[29 empty] | Cv / Kvs : |  | [l/s] [m3/h] | 9 | 32.4
[29 empty] | K : |  | [-] | 9.526
RESULTS
[29 empty] | Flow (Q) | Cv | Opening | Velocity | Headloss - Valve Fully open
[29 empty] | [l/s] | [%] | [%] | [m/s] | [Bar]
[28 empty] | Q min. | 0 | 0 | 0 | 0 | 0
[28 empty] | Q max. | 3 | 19.245 | 34.0599 | 1.5278 | 0.11117
Comments:
Enter notes here…
Cla-Val UK
GOODS STATION ROAD, TUNBRIDGE WELLS, KENT TN1 2DH
TEL : +44 (0) 1892 514 400 FAX : +44 (0) 1892 543 423